Andhra Pradesh Electricity Regulatory Commission

11-4-660, 4th and 5th floors, Singareni Bhavan, Red hills, Hyderabad

O.P.No. 179 of 2003

Dated: 08-04-2003

Present:

Sri. G.P.Rao, Chairman

Sri. D.Lakshminarayana, Member

Sri. K. Sreerama Murthy, Member

Transmission Corporation of Andhra Pradesh Limited (APTRANSCO)







…….. Applicant

As a sequel to the order of APERC in OP 506 / 2002 dated 29th July 2002, APTRANSCO filed a petition dated 28th January 2003 requesting the Commission’s approval for a new load forecast for the planning period FY 2002-2008 estimating the additional capacity requirement at 5251 MW citing certain additional factors responsible for the increase. 

The Commission passed the following order on the petition after considering the material available on record.

ORDER
1) Commission’s order dated July 29th 2002 on Load forecast

The Commission in the above-mentioned order directed APTRANSCO as follows:

(i) The system peak demand in the year FY 2006-07 shall be fixed at 10207 MW and energy requirement at 58776 MU after considering historical growth rates, system load factor of 70% and reserve margin of 14%.

(ii) The cumulative capacity required to be added during the planning period FY 2002- 2007 shall be 3180 MW as against 4270 MW projected by APTRANSCO

(iii) APTRANSCO shall revise the procurement plan to match the capacity of 3180 MW, as projected by the Commission

(iv) APTRANSCO shall include 250 MW of NEDCAP projects, MPPS, CC-5, NTPC Talcher II and NTPC Ramagundam Extension project to cover the demand forecast drawing up a least cost generation plan

(v) APTRANSCO and APGENCO shall consider the prospects of Srisailam Left Bank Project not contributing to the system peak and suggest equivalent capacity required, if any

2) APTRANSCO’s petition dated 28th January 2003

APTRANSCO has revised the capacity requirements to 5251 MW for the period 2002-2008, although no capacity was proposed to be added in FY 08, after adopting the growth rates and system load factor of 70% proposed by the Commission and taking the following additional factors into account:

(a) 24 hours rural supply which requires additional supply of power of about 1500 MU per year

(b) The targeted Loss of Load Probability (LOLP) of 1% which is expressed in hours per year as 87.6 hours /year

(c) Effect of Almatti which reduces the generation from Srisailam and Nagarjun Sagar by about 1000 MU per year due to lower inflows

(d) Srisailam Left Bank Power House contribution to the firm energy in conventional mode is NIL.

(e) To reduce the unserved energy to a level of 0.15% by the end of the planning period FY 2007.
3) The Licensee submitted a load forecast and a generation expansion plan along with the petition, which have been revised on 07-02-03 and again on 10-03-03. The licensee also submitted a business plan on 07-02-03, which was also subsequently revised on 10-03-03.

Commission analysis on the Demand of the AP System

4) Sales Projection for AP System 

The Commission, in its order dated 29th July 2002, while following a historical method has approved a growth rate of 6.9% and energy requirement of 58,776 MU and capacity requirement of 11636 MW at the end of the plan period FY 07. 

5)
In the letter dated 28th January 2003, the licensee has accepted the Commission’s growth rates and adopted the same for the planning period. However, it has incorporated the following changes:

(a) Additional requirement of 1500 MU from FY 2005 is considered to extend continuous supply of power to rural areas. 85% of this additional requirement is attributed to Domestic category and the balance to Commercial category.

(b) Reduction in loss levels to reflect the actual reductions vis-à-vis earlier projections

(c) Adopted ARR forecasts for the years FY 2003 and FY 2004 as submitted by the Licensees in December 2002 filings

6)
The Commission agrees with the licensee’s submissions of additional requirement of power due to provision of 24 hours rural supply, that being the policy of Government of Andhra Pradesh. However, the Commission is of the opinion that the costs related to such policy decisions need to be addressed in the Business plan. 

7)
The Commission is also of the view that the earlier projections needed to be adjusted to the actuals as filed in the ARR. The detailed break-up of the sales forecast presented by APTRANSCO and accepted by the Commission is enclosed as Annex I.

8)
Based on the above sales forecast, AP system requirement works out to be 61,017 MU at the end of the plan period FY 2007. 

System Load factor: 

9)
Though the present monthly system load factor ranges from 80 to 88% in the AP System, the Commission has proposed in its earlier order to adopt 70% as annual system load factor. 

10)
The licensee has agreed with the Commission’s viewpoint and has taken 70% as annual system load factor for projecting system capacity requirement as against its earlier claim of 66%.

Reliability: Loss of load probability (LOLP) & Unserved Energy: 

11)
APTRANSCO has adopted a target Loss of Load Probability (LOLP) of 1% i.e. 87.6 hours/year as the measure of reliability in estimating reserve capacity. This is to take care of the probability of failure of plants during the system peak demand. They have also proposed that the Energy Not Served (ENS) should be at a level of 0.15% of the energy requirement by the end of FY 2007. 

12)
In the Order dated July 29th 2002, the Commission has adopted 14% reserve margin as earlier suggested by APTRANSCO to achieve targeted LOLP of 1% for the planning period FY 2002-2007. In the later submissions dated 28th January 2003, the licensee has worked out a reserve margin ranging from 13% in FY 2002 to 28% in FY 2007 to achieve the targeted 1% LOLP.

13)
The Commission accepts the target of 1% LOLP and 0.15% of ENS as proposed by APTRANSCO, being the norms adopted by CEA for planning the capacity additions. However, to ascertain the reserve margin required for a target of 1% LOLP, the Commission has requested the Central Electricity Authority, as a technical consultant, to advise on the technical aspect of assessing the reserve margin and generating capacity requirement to attain LOLP of 1% and less than 0.15% ENS in the AP system. Based upon the information made available by APERC and APTRANSCO, studies have been carried out by CEA, which vide their report dated 17th March 2003 made the following recommendations to AP Commission:

(a) 16th Energy Power Survey (EPS) forecast should be the minimum requirement for power planning as against APTRANSCO’s projections

(b) Reserve margin of 30% in terms of rated capacity over peak demand or 29% of net capacity would give 1% LOLP and less than 0.15% ENS for the AP system.

(c) Additional projects, besides 5251 MW, totalling to a capacity exceeding 1300 MW needs to be identified to meet the demand projections as per the 16th EPS.

(d) Possibility of advancing the schedule of commissioning of projects due in 11th plan like Vijayawada VII unit (660 MW) may be seriously considered.

14)
The Commission notes that the actual demand and the load forecast by APTRANSCO is much lesser than CEA’s estimates of 16th EPS. Hence, the Commission didn’t consider the additional requirement of 1300 MW. Incidentally, the additional requirement would also involve substantial extra costs in the system, which has to be recovered by way of tariffs or subsidy.

15)
With regard to LOLP, the Commission agrees to adopt CEA’s recommendations on reserve margin of 29% of net capacity to give 1% LOLP and less than 0.15% ENS for the AP system, CEA being the highest technical authority.

16)
The Commission has further requested the CEA to suggest the required reserve margin in the following two situations:

(a) If only 300 MW of Srisailam left bank is considered in the capacity addition

(b) If no capacity of Srisailam left bank is considered in the planning period

CEA has responded that under APTRANSCO’s demand projection there would be a requirement of 32% reserve margin if only 300 MW is considered from SSLB project and 29% reserve margin if No MW is assumed from SSLB for the capacity addition.

17)
As SSLB has been excluded, for reasons stated in the supply section of this order, for determining the capacity requirement for the state of Andhra Pradesh, the Commission has considered 29% as reserve margin to achieve 1% LOLP and 0.15% of ENS in the AP system. 

Capacity Requirement in the planning period:

18)
The sales figures of the Distribution Companies approved by the Commission are added to the captive and wheeling consumers’ consumption, and this provides the total AP system consumption. By applying system load factor of 70% and system reserve margin of 29% as suggested by CEA, Commission has arrived at the system installed capacity requirement for the plan period as at Annex II.

19)
Commission has worked out the existing system capacity after deducting the auxiliary consumption for each of the generating units. The captive and wheeling capacity has been matched on the supply side to cater to the exact demand from these units on to the system. The gross installed capacity so arrived is 9210 MW in FY 2002 as detailed in Annex III.

20)
The resultant demand-supply situation is provided in the Table 1 below:

Table 1

	All figures in MW
	FY 02
	FY 03
	FY 04
	FY 05
	FY 06
	FY 07

	Installed Capacity 
	11,519
	11,623
	11,846
	12,525
	12,946
	13,639

	Existing Capacity
	9,210
	9,220
	9,235
	8,646
	8,457
	8,457

	Annual Additions required
	2,309
	94
	207
	1,269
	610
	693

	Cumulative Capacity required
	2,309
	2,403
	2,610
	3,879
	4,489
	5,182


21)
It may be recalled that APTRANSCO had estimated requirement of 5251 MW in the supply expansion plan. Against this, Commission has come to the conclusion that the system requirement of additional capacity is 5182 MW during the plan period 2002-2008.

22)
The reason for increasing the capacity requirement to 5182 MW from         3180 MW is on account of 24 hours rural supply and increase in reserve margin from    14% to 29%. 

23)
Hence, the Commission approves the following:

(a) The System peak demand for the year FY 2006-07 is 13639 MW and the energy requirement is 61017 MU.

(b) The cumulative capacity required to be added during the period 2001-02 till 2006-08 is 5182 MW.

(c) The annual capacity addition required is as provided in the Table1 above.

Supply Expansion - Commission Analysis

24)
APTRANSCO has submitted a revised supply expansion plan along with the Business Plan on March 10th 2003. They presented the following supply expansion plan shown in Table 2:

Table 2

	
	Projected Peak Demand
	Capacity Retirement
	Thermal Capacity Addition
	Hydel Capacity Addition
	Total Capacity Addition
	Total Net Capacity

	2001-02
	8927
	
	CC-1 (213.4) + Simhadri-I (460) + MPP (72) + NEDCAP (80.3) 
	298 Sri Sailam 
	1124
	9999

	2002-03
	9061
	
	Simhadri-Unit-II  (460) + New Captive 84.4 + NEDCAP (46.2)
	298 Sri Sailam 
	889
	10888

	2003-04
	9513
	
	NEDCAP (45.5)+ 98 Talcher
	298 Sri Sailam 
	442
	11329

	2004-05
	9763
	560 (400 Eastern region and 160 Captive)
	CC-2 (432) + MPP (54) + 98 Talcher
	
	584
	11352

	2005-06
	10143
	169 Captive
	CC-3 (359) + CC-4 (450.1) + CC-5 (213) + Talcher (98) + Ramgundam (134)
	
	1254
	12438

	2006-07
	10575
	
	385 RTPP + BPL (475.6) + 98 Talcher
	
	959
	13398

	Total (MW)
	
	728
	4357
	894
	5251
	


(Source: APTRANSCO Submission January 2003 Table: Power Procurement Plan)

25)
It is important to note the following facts from the above submission:

i) The supply expansion plan has been revised to 5251 MW in the petition dated 28th January 2003 to include 24 hours rural supply and increased reserve margin. 

ii) As directed by the Commission, APTRANSCO has considered NEDCAP and MPP’s capacity in meeting the peak requirement

iii) Entire 894 MW of Srisailam plant is included as capacity addition

iv) NTPC-Talcher-II and NTPC-Ramagundam-II are included in the capacity planning 

v) The Commissioning schedule of the new plants and year of captive repatriation are modified. Revised schedule of the new plants is shown in the table 3 below.

26)
APTRANSCO has agreed with the Commission’s viewpoint that due to hydraulic constraints in the riverbed, it will not be possible to start pumped mode operation from SSLB till 2007. They have also stated that it would take 6 years to eliminate these constraints. 

27)
As the contribution from SSLB for the peaking purpose is negligible, Commission directs APTRANSCO to exclude 894 MW of SSLB from the proposed capacity addition. Therefore, as no MW will be considered from SSLB, the Commission has taken 29% as reserve margin to achieve 1% LOLP as recommended by CEA.

28)
APTRANSCO has forwarded the following PPAs to the Commission for their consent to the PPA as per Section 21 (4) of the Reform Act.

Table 3

	Projects Under Scrutiny
	Capacity (MW)
	Commissioning Date

	BPL
	520
	FY 2007

	RTPP-II
	420
	FY 2007

	BSES
	220
	FY 2002

	Konaseema
	445
	FY 2004

	Vemagiri
	370
	FY 2006

	Gautami
	464
	FY 2006

	GVK Industries
	220
	FY 2006


29)
The following new projects, as submitted by APTRANSCO, that will come up during the planning period contribute about 4272 MW as against the additional installed capacity requirement to meet the peak demand of 5182 MW, leaving a gap of 910 MW in the plan period FY 2002-2007.

	New Generating Stations
	Capacity in MW

	BSES
	213

	Simhadri
	920

	MPP's
	126

	NEDCAP
	172

	GVK Extension
	213

	Talcher
	392

	Ramagundam Extension
	134

	Konaseema
	432

	Vemagiri
	359

	Gowthami
	450

	BPL Ramagundam
	476

	RTPP
	385

	Total Capacity
	4272


Analysis of the Business Plan

30)
Before approving the load forecast and procurement plan, the Commission has also analysed the Business Plan, especially with regard to the Power Purchase Cost. The significant observations made from the business plan include:

(i) The Business plan has considered 5251 MW of capacity addition including SSLB for the plan period FY 2002-07. The Business plan proposes to meet the total expenditure by way of Tariff increases, Government Subsidy, Efficiency measures and Other income viz. revenue from wheeling charges, sales of surplus power etc.

(ii) From the capacity addition considered, it is evident that the Business                   plan has also considered 29% reserve margin to provide reliable supply throughout the year for the state of Andhra Pradesh. It also includes 24 hours supply to rural domestic and commercial consumers.

(iii) The Business plan assumes that the gas projects will have supply of gas at the base price of Rs 2850 / 1000 SCM. This works out to about Rs 4000 / 1000 SCM inclusive of taxes and transportation. The Commission after discussions with the GAIL authorities had an apprehension that with the dismantling of Administrative Price Mechanism (APM) the gas prices might go up in future to Rs 5600 / 1000 SCM, the market determined rate now fixed for Ravva Satellite gas. At this rate the cost of gas works out to about Rs 7400 inclusive of taxes and transportation. In this context, the Commission expressed the following concerns to APTRANSCO vide its Lr.No.APERC/Secy/F:/ D.NO.874/03 dated 24-03-2003:

(iv) With the increase in gas prices, the power purchase cost of APTRANSCO in the plan period will be increased by Rs 1896 crores vis-à-vis the business plan projections (FY 2005-07) which needs to be addressed by the licensee 

(v) The increase in gas prices will also be applicable to the existing stations viz. Lanco Kondapalli, GVK, Spectrum, APGPCL etc. Hence, the variable cost of these stations will also increase and make them expensive in the merit order operations when compared to new gas plants and coal fired plants viz. APGENCO, CGS etc. In view of the dispatch rights provided to these IPP’s, other generating stations with lower variable costs might have to be backed down in the merit order.

(vi) The business plan projected seasonal surplus and assumes to sell about 2000 MU in FY 2006 and 4600 MU in FY 2007 to generate a revenue of Rs 1300 Crores. With regard to surplus power, the Commission is of the view that even after selling 4600 MU, there would be about 8000 MU surplus energy available for the state of Andhra Pradesh.

31)
APTRANSCO responded to the above as follows vide their letter number  CE/Trg.Plg./F.Load Forecast/D.NO 174 / 2003 dated 29-03-2003

(i) APTRANSCO is of the view that no firm decision is reached yet and in the event of any gas price increase especially from Ravva II satellite field, the increase will be spread over the entire allocation of gas there by impacting only to the extent of Rs 360 / 1000 SCM. APTRANSCO stated that this impact tantamount to Rs 300 Crores which will be recovered through the Fuel Surcharge Adjustment.

(ii) With regard to backing down of existing stations, APTRANSCO has responded that the AP Power Sector will become surplus only in the FY 2006, that too for short periods of time during the year, provided all the capacity additions materialise as scheduled. And hence, the situation of backing down the gas-based units to the extent of rendering them idle in a shortage scenario will not arise.

(iii) In response to the surplus energy, APTRANSCO pointed out that the surplus availability estimated by the Commission is only seasonal and there will be no surplus of 8000 MU’s left. They have also stated that the success rate of power projects in achieving financial closure is unimpressive in AP as well as in the entire country.

32)
Conclusions of the Commission 

(i) The Commission agrees that as of today the increase proposed in gas prices to the existing consumers is Rs 360 / 1000 SCM. However, APTRANSCO should be prepared for higher prices with the dismantling of APM and consequent higher power purchase costs. The Commission also acknowledges that with the existing level of gas prices, the Business plan has tied up the entire expenditure by way of Subsidy, Tariff Revenue and Non-Tariff income. 

(ii) As per the Commission’s workings it is evident that even after selling 4600 MU of surplus power during FY 07, there will be surplus availability of about 8000 MU for which there might not be any requirement. There will be substantial surpluses if all the projects go through as scheduled and if the export plans do not materialise. The surplus availability indicates that few stations have to be kept on standby paying only the fixed charges. APTRANSCO and GoAP should be prepared for this situation and should have a contingency plan to meet the eventualities. This situation arises primarily on account of the provision of considerable reserve margin of 29% to achieve the level of reliability at the accepted targets of 1% LOLP and 0.15% ENS. The Commission emphasises that, while it is desirable to have a reserve margin of 29% as sought by the Licensee and as confirmed by CEA, to ensure reliable supply, it should be realised that it has a cost as most of the time some capacity be standing by.

(iii) CEA has also corroborated in its report that few stations are not expected to operate at 85% system load factor and would operate at below 1% load factor. However, CEA has also indicated that the achievement of capacity addition under private sector is highly unsatisfactory and keeping this uncertainty in view, it would be prudent and pragmatic to plan for higher capacity addition.

(iv) Commission agrees with the CEA’s statement and acknowledges that if some of the projects do not achieve financial closure, to that extent the reserve margin will come down. This correspondingly reduces the financial burden although it will have an adverse effect on the reliability of supply.

(v) The Commission also notes that with the increase of gas prices to      Rs7400, the variable cost of the new gas stations will be increased from about 80 ps/kwh to about 150 ps/Kwh. In spite of this increase, the average cost from these plants will be about Rs 2.50/kwh which will be more or less on par with the coal plants like BPL, RTPP etc and it will increase the average cost of power purchase of APTRANSCO by 11 ps/kwh. To the extent exports take place, the burden of power purchase cost will go down.

ORDER

33)
In the facts and circumstances mentioned above, the Commission directs as under:  

(a) In terms of Section 11 (1) (g) of the Reform Act, the System peak demand in the year FY 2006-07 shall be fixed at 10575 MW and the energy requirement at 61017 MU.

(b) For meeting the peak load and energy requirement, the installed capacity at the end of the planning period will be 13639 MW. 

(c) The annual capacity addition required shall be as provided in the Table1 above. The cumulative capacity required to be added during the period 2001-02 till 2006-07 shall be 5182 MW.

(d) Based on the capacity requirement of 5182 MW, Commission approves the power procurement plan of APTRANSCO as detailed in Table 2 excluding SSLB from the capacity addition to meet the peak requirement.

(e) APTRANSCO may exclude the cost of SSLB project from the Business Plan till the capacity can be recognised for meeting the peak requirement.

(f) Inclusion of new plants proposed in the approved power procurement plan doesn’t construe approval of the Power Purchase Agreements for these new plants by the Commission. Approval of PPA by the Commission depends on the merits of the agreement and is not part of this order.

(g) As per the paragraph 2.2 of the power procurement guidelines the licensee shall submit its load forecast to the Commission in the month of April of each year.

(This Order is signed by the Andhra Pradesh Electricity Regulatory Commission on  8 April 2003)

           Sd/-



   Sd/-




    Sd/-

(K Sreerama Murthy)
      
   (D Lakshminarayana)


(G P Rao)

        Member


           Member



Chairman

CERTIFIED COPY

Annex I: Commission Approved Sales Forecast

In Million Units

	
	FY 01
	FY 02
	FY 03
	FY 04
	FY 05
	FY 06
	FY 07
	CAGR

	Domestic
	    6,117    6,117 
	6,698
	      7,583  7,583 
	8,206
	10,552
	11,775
	13,147
	13.60%

	Commercial
	1,273
	1,397
	1,628
	1,814
	2,177
	2,430
	2,713
	13.44%

	LT Industry
	1,680
	1,756
	2,037
	2,241
	2,557
	2,910
	3,313
	11.98%

	Cottage Industry
	31            31 
	28
	            31 
	            34 
	            39 
	            44 
	            50 
	8.29%

	Irrigation and Agriculture
	11,071
	12,181
	11,237
	10,998
	10,888
	10,778
	10,670
	-0.61%

	Public Lighting
	407
	520
	653
	 697          697 
	872           872 
	973
	1,085
	17.75%

	General purpose
	122
	80
	            91 
	109
	122
	136
	152
	3.73%

	Temporary
	2              2 
	7
	            11 
	            13 
	            14 
	            16 
	            18 
	44.22%

	TOTAL LT
	      20,703 
	22,667
	      23,271 
	      24,112 
	      27,221 
	      29,062 
	      31,148 
	7.04%

	
	
	
	
	
	
	
	
	

	Industrial Segregated
	3,646
	3,746
	4,764
	5,417
	5,849
	6,318
	6,824
	11.01%

	Industrial Non-Segregated
	602
	616
	736
	818
	906
	1,001
	1,109
	10.72%

	Irrigation and Agricultural
	39
	44
	79
	175
	183
	192
	202
	31.54%

	Railway Traction
	922
	963
	1,094
	1,155
	1,244
	1,342
	1,446
	7.79%

	Colony lighting
	128
	180
	178
	195
	206
	215
	225
	9.86%

	RESCO's
	1,147
	1,123
	1,152
	1,166
	1,247
	1,335
	1,426
	3.70%

	HT TOTAL
	3,646
	3,746
	4,764
	5,417
	5,849
	6,318
	6,824
	11.01%

	Overall Demand
	27,187      27,187 
	29,339
	31,274
	33,038
	36,856
	39,465
	42,380
	7.68%


Annex II: Capacity and Energy requirement for AP Power System

	
	
	FY 02
	FY 03
	FY 04
	FY 05
	FY 06
	FY 07

	DISCOMS Sales (LT+HT)
	MU
	29,339
	31,274
	33,038
	36,856
	39,465
	42,380

	APTRANSCO Purchases
	MU
	42,214
	42,870
	43,904
	47,251
	49,331
	52,646

	Wheeling Energy Requirement
	MU
	3,650
	3,296
	3,322
	3,205
	3,125
	3,106

	Captive Repatriation energy requirement
	MU
	-
	-
	-
	786
	1,533
	1,523

	Outstanding Captive
	MU
	4,921
	5,026
	5,026
	4,384
	3,742
	3,742

	System Energy Requirement
	MU
	50,786
	51,193
	52,253
	55,627
	57,731
	61,017

	
	
	
	
	
	
	
	

	System Load Factor
	
	70.00%
	70.00%
	70.00%
	70.00%
	70.00%
	70.00%

	
	
	
	
	
	
	
	

	APTRANSCO Capacity Requirement
	MW
	6,884
	6,991
	7,160
	7,706
	8,045
	8,585

	Capacity Requirement for wheeling
	MW
	595
	538
	542
	523
	510
	506

	Captive Repatriation 
	MW
	-
	-
	-
	189
	378
	378

	Outstanding Captive
	MW
	1,450
	1,481
	1,481
	1,292
	1,103
	1,103

	System Peak Demand Requirement
	
	8,930
	9,010
	9,183
	9,709
	10,035
	10,573

	System margin for 1 % LOLP
	29%
	2,590
	2,613
	2,663
	2,816
	2,910
	3,066

	System Installed Capacity Requirement
	
	11,519
	11,623
	11,846
	12,525
	12,946
	13,639


Annex III: Capacity of Existing units:

	Generating Units
	Installed Capacity
	Auxiliary Consumption
	Capacity Available

	
	
	
	

	APGENCO
	
	
	

	   -  Thermal units
	2,953
	10%
	2,657

	   -  Hydel units
	2,672
	1%
	2,645

	
	
	
	

	Central Sector
	1,000
	
	

	   -  NTPC
	580
	8.43%
	531

	   -  NEYVELI
	277
	8.43%
	254

	   -  MAPP
	28
	8.43%
	26

	   -  Kaiga
	115
	8.43%
	105

	
	
	
	

	Vijjeswaram
	
	
	

	    -  VGTS-I
	100
	3%
	97

	    -  VGTS-II
	172
	3%
	167

	
	
	
	

	Independent Power Producers (IPPs)
	
	
	

	   -  GVK
	216
	3%
	210

	   -  Spectrum
	208
	3%
	202

	   -  Kondapalli
	355
	3%
	344

	
	
	
	

	GRIDCO / Eastern Region
	
	
	400

	
	
	
	

	Captive and Other Wheeling Consumers
	
	
	1483

	
	
	
	

	Non Conventional Projects
	
	
	90

	
	
	
	

	TOTAL
	
	
	9210













































































PAGE  
17

